



**Measuresoft Development Ltd.**

**Solartron IMP Driver Manual**

**Version:** **6.8.0.0**

Configuration of Solartron IMP Modules

Introduction to Configuration 3

Launching the Device Configuration Utility 5

Channel Device Specific Configuration 7

To Configure an IMP Module 7

Steps to Configure 35951A / 35951B / 35951C / 35951D / 35951E /First 18 3595 1H/1J/35951Q Channels 10

Steps to Configure a 35952A, 3595 2B or Last 2 channels of 3595 1J/1H 13

Channel Device Specific Configuration Fields 16

Enable Alarm Checking 17

Drive Common Alarm 18

Drive CH 19 and Drive CH20 18

Alarm Limit 18

Warning and Limit (Analogue channel only) 18

Hysteresis 18

Priority 18

Alarm Delay 18

Alarm Message 18

Buttons on the Configuration Dialogs 25

Interrogating IMP Modules 27

To Interrogate IMP Modules 27

Read 27

Calibrate 27

Steps to Calibrate an IMP Module 28

Advanced Configuration 30

Steps for Carrying Out Advanced Configuration 30

Advanced Device Specific Configuration Fields 31

To Add a Calibration Polynomial 32

To Edit a Calibration Polynomial 33

To Delete a Calibration Polynomial 33

Error Codes 34

## Introduction to Configuration

To configure IMP channels, you must firstly choose an IMP module to configure and then configure the channels within that selected module. The configuration of IMP channels varies depending on the :

1. Type of IMP module selected
2. The Mode a particular channel is in

Below is a list of IMP modules, their type, the number of channels within that module and what the module supports

|  |  |  |  |
| --- | --- | --- | --- |
| ***Module Name*** | ***Module Type*** | ***No of Channels*** | ***Supports*** |
| 35951A | Analog Input | 20 | Thermocouples, Voltage, Current |
| 35951B | Analog Input | 10 | Strain Gauges, PRT’s, Voltage, Resistance |
| 35951C | Analog Input | 20 | Thermocouples, Voltage, Current |
| 35951D | Analog Output | 4 | Voltage, Current |
| 35951E | Analog Input | 20 | Thermocouples,Voltage, Current |
| 35951H/1J | Universal ImpAnalog Input and 2 Digital I/O | 20 | Thermocouples, Voltage, CurrentPRT’s, ResistanceStatus, Events, Frequency, etc. |
| 35951Q | Analog Input | 20 | Thermocouples, Voltage, Current, Strain Gauges, PRT’s, Resistance |
| 35952A | Digital Input, Digital Output, Counter Input | 20 | Status, Events, Frequency, etc. |
| 35952B | Digital Input, Digital Output, Counter Input | 32 | Status, Events, Digital Output |

The steps needed to configure a particular channel within a particular module will be examined. Different dialogs are displayed depending on the IMP module type. Different fields are displayed on each dialog depending on the Mode of the channel.

The following is explained :

|  |
| --- |
| Steps to Configure a 35951A/35951B/35951C/35951D/35951E IMP Channel |
| Steps to Configure a 35952A/2B IMP Channel |
| List of fields on particular configuration dialogs |
| Explanation of those fields |

## Launching the Device Configuration Utility

**To Start the Device Configuration Utility :**

1. Choose the ***Solartron IMPS*** option from the ***Devices***  menu. The following application window will appear.

Click on the ***Module Configuration*** Tab to get a list of the modules on the network.



1. You can now configure the IMPs using the various options

***Fields on the Module Configuration Tab***

A list of Channels, Module names, Module types, Addresses and Scan Rates are visible on the window.

***ChannelRange***

There can only be a maximum of 1000 channels on any IMP network

***Module Name***

This refers to the name of the IMP module. There are 7 IMP module types :

|  |
| --- |
| 1. 35951A
 |
| 1. 35951B
 |
| 1. 35951C
 |
| 1. 35951D
 |
| 1. 35951H/1J
 |
| 1. 35951E
 |
| 1. 35951Q
2. 35952A
3. 35952B
 |
|  |

***Module Type***

IMP Modules will be one of the following :

|  |
| --- |
| 1. Analog Input
 |
| 1. Analog Output
 |
| 1. Digitals
 |

***Address***

This is the physical address of the IMP on the IMP network. Addresses range from 1 to 50. There can only be a maximum of 50 IMP modules on any IMP network.

***Rate***

This refers to the scan rate (acquisition rate). This can be SLOW or FAST.

## Channel Device Specific Configuration

Before configuring a channel, you must firstly configure a module

### To Configure an IMP Module

1. Click on a ChannelRange in the **Module Configuration** Tab of the main Solartron IMPs configuration window.
2. The following dialog will appear :



***Fields on the Configure IMP Module Dialog***

***Module Type***

This field allows you to specify the type of IMP module you wish to configure. Options here are :

|  |
| --- |
| 1. INACTIVE
 |
| 1. 35951A
 |
| 1. 35951B
 |
| 1. 35951C
 |
| 1. 35951D
 |
| 1. 35951E
 |
| 1. 35951H/1J
 |
| 1. 35951Q
 |
| 1. 35952A
 |
| 1. 3595 2B
 |

***Acquisition Rate***

This specifies the rate at which scanning occurs. You can choose SLOW or FAST.

**Temperature Reference and Thermocouple Checking**

These fields can only be set when you are configuring particular types of IMP module

|  |  |
| --- | --- |
| ***Module Type*** | ***Temp. Ref & Thermo. Checking Available*** |
| 35951A | ✓ |
| 35951B | 🗶 |
| 35951C | ✓ |
| 35951D | 🗶 |
| 35951E | ✓ |
| 35951H/1J | ✓ |
| 35951Q | ✓ |
| 35952A | 🗶 |

***List Of Channels***

A list of all the channels that can be configured is displayed here. The number of channels displayed depends on the type of module you are configuring (See diagram in the introduction for the number of channels in each module type.

Foe each channel, the following information is displayed :

|  |
| --- |
| 1. System Channel
 |
| 1. Tag
 |
| 1. Description
 |

***Mode***

Sets the mode for all Imp channels automatically at module level and overrides any manually configured mode. If you manually change one of the imp channels after setting the mode from this menu, the Mode drop down box will appear blank to represent that not all the channels are the same.

***Range***

Sets the range for all Imp channels automatically at module level and overrides any manually configured range. If you manually change one of the Imp channels after setting the range from this menu, the range drop down box will appear blank to represent that not all the channels are the same.

***System Channel***

Displays the mapping of an IMP channel to a system channel

***Tag***

A tag is a twelve character alphanumeric field that can contain channel information. This field will contain *Skipped* (i.e. Channel not configured) or a valid tag

***Description***

Your description of the channel

The currently highlighted channel is also shown in the Channel Number field.

We can now examine how to configure individual channels on each of the IMP modules

### Steps to Configure 35951A / 35951B / 35951C / 35951D / 35951E /First 18 3595 1H/1J/35951Q Channels

1. Choose the module type on the configure IMP module dialog
2. If available, Temperature Reference can be set to Ambient or External.

 Thermocouple Checking can also be enabled

1. For each module the number of available channels will be visible in the channel listings.
2. Select a channel to configure by :

Double Clicking the desired channel with the mouse

**OR**

Click on the desired channel and click the ***Configure Channel*** button at the bottom of the Configure IMP Module dialog.

The following dialog will then appear for 35951A, 35951B, 35951C, 35951E, 35951Q, and the first 18 channels of the 3595 1H/1J:



1. The following dialog will then appear for 35951D :

:

See section entitled *“Channel Device Specific Configuration Fields”* for an explanation of each field.

6. Choose either **OK** or **CANCEL** button to return to the “Configure IMP Module”

 dialog.

7. If desired the changes to the configuration can be saved, or discarded by exiting the

 configuration utility without saving. Only changes to configuration which have

 been saved will be used by the system.

8. In order for the changes to take effect, the system must reload the configurations

 and restart the device scanner. For channel specific changes this requires calling

 only the reconfigure command from the Control menu either in main menu or the

 Configuration utility. For Advanced configuration changes described in this

 section, the system must be disabled and re-enabled for the changes to take effect.

9. The configuration of the channel is now complete.

**Note :**

See section entitled “*Buttons on the Configuration Dialogs”*

### Steps to Configure a 35952A, 3595 2B or Last 2 channels of 3595 1J/1H

1. Choose the ***35952A*** module type on the configure IMP module dialog
2. Temperature Reference and Thermocouple Checking cannot be used
3. 20 channels will be visible in the channel listings.
4. Select a channel to configure by :

Double Clicking the desired channel with the mouse

**OR**

Click on the desired channel and click the Configure Channel button at the bottom of the Configure Module dialog.

1. A dialog appears. Different fields are displayed depending on the selected Mode.

Note that when using a 3595 4B or 4C SNet interface, events captured from 2A Imp modules are stored in <product dir>\LOGGED\_IMP\_EVENTS\YYMMDD\rtmeHH00.log files.

1. This dialog represents *Digital Input, Digital Output and OFF modes*



This dialog represents all other modes on the 31952A :



See section entitled *“Channel Device Specific Configuration Fields”* for an explanation of each field

9. Choose either **OK** or **CANCEL** button to return to the ***Configure IMP Module***

 dialog.

10. If desired the changes to the configuration can be saved, or discarded by exiting

 the configuration utility without saving. Only changes to configuration which have

 been saved will be used by the system.

11. In order for the changes to take effect, the system must reload the configurations

 and restart the device scanner. For channel specific changes this requires calling

 only the reconfigure command from the Control menu either in main menu or the

 Configuration utility. For Advanced configuration changes described in this

 section, the system must be disabled and re-enabled for the changes to take effect.

12. The configuration of the 35952D IMP channel is now complete.

See section entitled “*Buttons on the Configuration Dialogs”*

When finished configuring channels you will be at the ***IMP Device Configuration*** dialog.

### Channel Device Specific Configuration Fields

This section contains an alphabetic list of all the possible fields that can be displayed on various configuration screens.

#### Alarms

**Alarm State**

Alarm checking is available on all channels throughout the system. To configure alarm checking on a channel, click on the drop down box and select : OFF, LOW STATE, HIGH STATE as appropriate.

If the channel output state changes to an alarm state an alarm will be triggered on the channel. When monitoring channels, if the alarm is triggered, the fact will be annotated alongside the other channel information in the monitor window

**Alarm Priority**

Use this to set the priority of the alarm triggered by the channel

**Common Alarm**

Channels can be configured to trigger a common alarm. A common alarm is a single digital output which will switch on when any channel with the Drive Common Alarm enabled goes into an alarm state.

**Alarm Message**

An alarm message can be defined to be displayed on the status line of the applications main window when a channel goes into an alarm state

#### Calib Poly

This refers to the calibration polynomial. These are set in the Advanced section of the configuration. The drop down list will contain a list of any added/created calibration polynomial

####

#### Description

The description field is a 16 character alphanumeric field in which a description of the channel can be detailed

#### Enable Channel

The Enable Channel check box must be checked to enable, and allow this channel to be configured and ultimately included with all other configured channels in the overall system

#### Event Checking

Event checking is used to trigger a logger to record information on a number of channels during an event. Check the Event Checking check box if this facility is required

**High Limit**

A value in engineering units entered in this text box will define the level that if exceeded will cause an event trigger

**Low Limit**

A value entered in this text box will define the level that if the channel result falls below will cause an event trigger

#### HighState Description

A 32 character field in which to enter a description of the high sate of the channel

#### Low Alarm Checking & High Alarm Checking

Alarm Checking is available on all channels throughout the system

Low alarm and High alarm levels can be configured independent of each other. All the values entered are in engineering units. If a channel reading exceeds the high alarm limit then an alarm will be triggered as it will if the channel goes below the low alarm limit

When monitoring channels, if the high or low alarm is triggered, then the fact will be annotated alongside he other channel information in the Monitor window.

### Enable Alarm Checking

Check either the Low Alarm Checking or High Alarm Checking or both check boxes to enable the facility.

### Drive Common Alarm

A common alarm is a single digital output which will switch on when any channel with the Drive Common Alarm enabled goes into an alarm state. Check this box if a link to the Common Alarm is required.

### Drive CH 19 and Drive CH20

Channel 19 and Channel 20 on 3595 1J/1H can be configured as an alarm digital output which will switch on/off when any channel with this field enabled goes into an alarm state.

### Alarm Limit

Specifies the value which will trigger this alarm. for Low Alarm Checking it will be any value <= the Alarm Limit and for High Alarm Checking it will be any value >= the Alarm Limit.

### Warning and Limit (Analogue channel only)

If required, a warning can be displayed when a channel reaches a limit close to the alarm limit. For low alarm checking, the limit must be less than the alarm limit. For high alarm checking, the warning limit must be less than the alarm limit

### Hysteresis

Hysteresis can prevent 'noisy' channels from reporting multiple alarms when the average reading is close to the alarm threshold. Check the box if this feature if needed. Enter the value of the dead band in the corresponding value field.

### Priority

Enter or edit the number in the text box to allocate the priority of this alarm. Alarm priority ranges are from 0 to 255.

### Alarm Delay

Enter the time, in seconds, between the channel value entering the alarm state and the system flagging an alarm.

### Alarm Message

An Alarm Message can be defined to be displayed on the Status line of the Main Window when a channel goes into an alarm state. Enter the message, up to 32 characters, that is to appear in the event of an alarm.

#### LowState Description

A 32 character field in which to enter a description of the low state of the channel

#### Measure Loop Resistance

If the channel mode on the first 18 channels of a 3595 1J/1H is set to thermocouple, it is possible to measure the loop resistance of the thermocouple. The loop resistance measurement is stored in the specified channel. It is recommended to use the User Analog channels e.g. for IM1 specify P1.

#### Mode

Choosing a Mode option from this drop down list will instruct the IMP module how the channel is to be measured and the readings interpreted. Conversion to engineering units occur automatically. The options available in the drop down list vary depending on the IMP module.

Mode is related to Range (The appropriate range for the measurement)

**Table : 31951A and 31951C Modes and Associated Ranges**

|  |  |
| --- | --- |
| ***Mode*** | ***Range*** |
| OFF | None Available |
| Volts | AutoRange20mV200mV2V10V |
| Thermocouple Type E, J, K, R, S, T, B, N | AutoRange20mV200mV2V10V |
| Current | AutoRangeMicroAmpsMamps20mAmpsmAmps |

***Table : 31951B Modes and Associated Ranges***

|  |  |
| --- | --- |
| ***Mode*** | ***Range*** |
| OFF | NONE AVAILABLE |
| Volts | AutoRange20mV200mV2V |
| Resistance, 4-term, 0.8mA drive | AutoRange25 Ohms250 Ohms2K 5 Ohms |
| Resistance, 3-term, 08mA drive | AutoRange25 Ohms250 Ohms2K 5 Ohms |
| RTD/PRT, 100Ohm, 4 TermRTD/PRT, 100Ohm, 3 Term1/2 bridge, 4mA dual current1/2 bridge, 0.8mA dual current1/4 bridge, 4 mA dual current1/4 bridge, 0.8mA dual currentFull bridge, 8mA driveFull bridge, 1.6 mA drive3-wire, 4 mA drive3-wire, 0.8 mA drive | AutoRange20mV200mV2V |

***Table : 31951D Modes***

|  |
| --- |
| OFF |
| Voltage -10V to +10V |
| Current 4 to 20 mA |

**Note :**

There are no Ranges with this type of module

***Table : 31951Q Modes***

|  |  |
| --- | --- |
| ***Mode*** | ***Range*** |
| OFF | None Available |
| Volts | AutoRange20mV200mV2V10V |
| Thermocouple Type E, J, K, R, S, T, B, N | AutoRange20mV200mV2V10V |
| Current | AutoRangeMicroAmpsMamps20mAmpsmAmps |
| Resistance, 4-term, 0.8mA drive | AutoRange25 Ohms250 Ohms2K 5 Ohms |
| Resistance, 3-term, 08mA drive | AutoRange25 Ohms250 Ohms2K 5 Ohms |
| RTD/PRT, 100Ohm, 4 TermRTD/PRT, 100Ohm, 3 Term | AutoRange20mV200mV2V |

***Table : 31952A Modes and Associated Ranges***

|  |  |
| --- | --- |
| ***Mode***  | ***Range*** |
| OFF | NONE  |
| Digital Input | NONE |
| Event Count TotaliseEvent Count IncrementEvent Capture | Edge :-ve going edge+ve going edge+ve going edge or -ve going edge |
| Digital Output | NONE |
| Frequency | Gate Time :10 ms100ms1 secs10 secs |
| Period | Period :1 period10 periods100 periods1000 periods |
| One-Shot | Pulse :-ve going start+ve going start-ve going stop+ve going stop |

#### Ref

When the reference check box is checked, the channel has been defined as a Reference channel. Values of a reference channel are displayed as the measured value - zero value. When the system is enabled, the zero value can be initialised using one of the following methods :

From the IMP Device Configuration window choose Initilise from the Control menu

From the application window choose initilise from the Control menu

Press keys : CTRL + I together

#### Sample Rate

This is the rate at which sampling occurs within the device. The options are :

 (a) 1Khz

 (b) 10Khz

 (c) 100Khz

 (d) 20 hz

 (e) Default

#### Scaling

To enable the utility, check the Scaling check box. The slope and offset values can be entered directly into the text boxes.

The formula applied is :

**y = mx + c**

Where :

m = Slope

x = Measured Value

c = offset

**AutoScale**

Click on the autoscale button if you want to scale and offset values calculated automatically. The following dialog is displayed :



Enter the values in the text boxes - the Low measured value, the High measured value and the Output range of the Transducer

Scaling will not be applied to the channel even if the system is enabled. Scaling will be applied when the system is re-enabled or the IMP device is reconfigured.

#### Sig.Change (Signal Change)

To enable the significant change feature, click he Sig. Change check box. This facility allows filtering of data on channels on which significant changes are of interest. Such changes cause an event which can be logged.

The figure entered in the value text box, in engineering units, is the rate of change that the measured channels exceed per scan. Either increasing or decreasing will cause the significant event trigger.

The scan rate is determined in the Advanced IMP device window. If a logger is configured in Event mode, or Period-Event, each time the significant change trigger occurs information on the channels defined in the logger will be recorded. A significant change event only lasts one scan, unless the next reading also changes greater than the significant change value.

When monitoring channels, if the significant change is triggered, then the fact will be annotated alongside the other channel information in the monitor window

#### Tag

The Tag is an 15 character alphanumeric field that can contain channel information.

#### Timeout

The timeout field is available when the Mode is Period or One-Shot. The options are :

 (a) 200ms

 (b) 2sec

 (c) 20sec

 (c) 50sec

#### Units

An 8 character field available to describe the units of the measurement

### Buttons on the Configuration Dialogs

Eight buttons are at the bottom of the Configure Analog Input Channel Window. They are explained below :

#### OK Button



When a channel has been successfully configured click on the OK button to accept and move back to the previous window.

#### Cancel Button



Clicking on the Cancel button will nullify any changes made. The configuration of that channel will remain unaltered. The previous window will be displayed.

#### Copy Button



If the configuration of the current channel is to be repeated, clicking on this button will copy the configuration to the Windows Clipboard.

#### Paste Button



When a configuration has been copied to the Clipboard it can be pasted into any other channel on this IMP Module by this button.

#### Previous & Next Buttons



Clicking on Previous or Next buttons will accept the current channels configuration and move on to either the next or the previous channels Configuration Window.

#### Goto Button



Selecting the Goto button will accept the current channels configuration and move on to the channel entered in the resulting **Goto Channel No.** dialog box.

#### Help Button



If any Help is required concerning any element of this window, clicking on this button will select the Help utility.

## Interrogating IMP Modules

### To Interrogate IMP Modules

1. Click the Network Modules Icon on the toolbar of the main application window. A dialog will appear.





You are presented with two lists :

List on the left-hand side are IMP’s actually on the S-Net

List on the right-hand side are configured modules

It is possible to have modules present on the S-Net which have not been configured as well as having modules configured which are not present on the S-Net.

Two options are available here :

### Read

The read option is only available if the IMP device is disabled. Clicking on the Read button will save some work in configuring the Imp module. It brings configuration information about inactive modules from the IMP into the system.

### Calibrate

This option allows you to calibrate an IMP module on the S-Net

### Steps to Calibrate an IMP Module

Click the Calibrate button on the IMP Modules dialog (after clicking the Modules button ion the IMP Device Configuration dialog)

The following dialog will appear :

**Imp Type**

This is the type of IMP module you are configuring (i.e. 31951A, B, C, D, E, 2A)

**Address**

This is the address of the IMP module on the S-Net

**CalibrationRange**

Ranges are only available for 35951A, B, C and Q

For 35951A, 31951C and 35951Q:

|  |
| --- |
| 1. 20mV
 |
| 1. 200mV
 |
| 1. 2V
 |
| 1. 10V
 |

For 35951B :

|  |
| --- |
| 20mV |
| 200mV |
| 2V |
| Resistance |
| 4mA strain gage |
| 0.8mA strain gage |
| 4mA strain gage |

## Advanced Configuration

### Steps for Carrying Out Advanced Configuration

1. Click the ***Advanced Configuration*** tab on the main ***Imp Configuration*** Application window. The following view will appear :



2. Fill in the fields as appropriate.

3. Select the appropriate communications method

ie 3595 4U USB Interface or 3595 4A/4B/4C PC to SNet Card.

Selecting the 3595 4UUSB Interface allows selection of the COM Port provided by the USB interface.

Selecting the 3595 9X interface allows entry of the interface IP address and interface card number.

4. Choose either the **OK** or **CANCEL** button to return to the ***IMP Device***

 ***Configuration*** dialog.

5. If desired the changes to the configuration can be saved, or discarded by exiting the configuration utility without saving. Only changes to configuration which have been saved will be used by the system.

6. In order for the changes to take effect, the system must reload the configurations and restart the device scanner. For channel specific changes this requires calling only the reconfigure command from the Control menu either in the Main Menu or the Configuration utility. For Advanced configuration changes described in this section, the system must be disabled and re-enabled for the changes to take effect.

7. Advanced configuration is now complete.

### Advanced Device Specific Configuration Fields

The advanced configuration dialog contains the following fields :

#### Enable Device

This allows you to start or enable your device/scanner

#### Fast Acquisition Rate

This is the rate data is scanned from fast modules.

#### Slow Acquisition Rate

This is the rate data is scanned from slow modules. Note slow data is interleaved with fast data so that there an acquisition speed is regular e.g. 2 fast modules at 1 second 2 slow modules at 2 seconds means 1 slow module is interrogated every second.

#### Loop Resistance Acquisition Rate

This is the rate loop resitance measurements are made from 3595 1H/1J modules. Note loop resistance data is interleaved with fast data so that there an acquisition speed is regular e.g. 2 fast modules at 1 second 2 thermocouples with loop resistance at 2 seconds means 1 loop resistance is interrogated every second.

#### Integration Time

Options for the integration time are :

 (a) 20.00ms for 50 Hz (or 400 Hz)

 (b) 16.67ms for 50 Hz

 (c) 5.00 for 400Hz

 (d) 4.17ms

 (e) 1.25ms

 (f) 1.04 ms

#### Temperature Results

From the drop down list, choose the temperature conversion required :

 (a) Degrees Centigrade

 (b) Degrees Fahrenheit

#### Calibration Polynomials

Underneath this heading is a window reserved for listing all set Calibration Polynomials.

For IMP’s the polynomials are of the form :

**ax5 + bx4+ cx3 + dx2 + ex1 + f**

Calibration polynomials are set here. Once setup, these polynomials will appear in the drop down list in the channel configuration dialogs (in the Calib. Poly. Field) of the following modules : 31951A, B and C.

Calibration Polynomials are listed with their name together with their associated parameters (a - f)

### To Add a Calibration Polynomial

1. Click the ***Add*** button on the ***Advanced Configuration*** Tab of the main application window. The following dialog will appear :



1. Enter a name for the polynomial together with the 7 parameters - a to f
2. Click the **OK** button to acknowledge or **CANCEL** to ignore
3. If OK is selected, the added polynomial will be appended to the list of existing polynomials or if none exist will appear as the first.
4. Choose either the **OK** or **CANCEL** button to return to the ***Advanced Configuration*** Tab of the main application window.
5. If desired the changes to the configuration can be saved, or discarded by exiting the configuration utility without saving. Only changes to configuration which have been saved will be used by the system.
6. In order for the changes to take effect, the system must reload the configurations and restart the device scanner. For channel specific changes this requires calling only the reconfigure command from the Control menu either in main menu or the Configuration utility. For Advanced configuration changes described in this section, the system must be disabled and re-enabled for the changes to take effect.
7. Once all the above is complete, Advanced configuration is finished.

### To Edit a Calibration Polynomial

1. Double Click on the desired polynomial in the ***Advanced Configuration*** Tab.
2. The ***Conversion Law*** dialog above will appear.
3. Modify the values as needed.
4. Choose OK to acknowledge or CANCEL to ignore.

### To Delete a Calibration Polynomial

1. Select the desired polynomial from the list on the ***Advanced Configuration*** Tab of the main application window using the mouse.
2. Press the ***Del***button on the ***Advanced Configuration*** Tab of the main application window.

3. The polynomial will be removed from the system.

## Error Codes

**Imp Errors**

|  |  |
| --- | --- |
| ***Error Code*** | ***Meaning*** |
| 43 | Timeout on Imps  |
| 44 | Error on response from Imps |
| 45 | S-Net not connected |
| 50 | Imp not present on S-Net |
| 51 | Error on Imp stream  |
| 52 | Too busy to configure S-Net |
| 53 | Too many S-Net read requests |
| 54 | S-Net command too long |
| 55 | S-Net voltage below minimum  |
| 56 | Cancel read failure |
| 60 | Input overflow |
| 62 | Command string too long |
| 70 | Invalid number  |
| 71 | Invalid hexadecimal |
| 72 | Unknown internal command |
| 73 | Parameter error |
| 74 | Invalid use of I\_RL  |
| 80 | Unable to return to local |
| 81 | Not in local |
| 99 | Error/Status lost |

For all other errors see WIN32 reference manual.