

Partnership Courtyard, The Ramparts,

Dundalk, Ireland

Version 6.8.0.0

March 7, 2022

www.measuresoft.com

+353 42 933 2399

This document is the copyright of Measuresoft and may not be modified, copied or distributed in any form whatsoever without the prior permission of Measuresoft.

Alpha Driver User Manual

Table of Contents

Configuring an Alpha Device 6

Advance Alpha Configuration 7

Alpha Scan Rate 7

Save Outputs 7

Listener Mode 8

Comm Port Settings 9

Network RS485 9

Single RS232 9

Comm Port 9

Baud Rate 9

Read Outputs when not writing 9

Read Outpts on initial scan 9

Use high speed 485 9

Event Logging 9

OK 10

Cancel 10

Configuring an Alpha Module 11

Module Type 11

Address 11

Acquisition Rate 11

Auxiliary Channels 12

Extra Command(n) 12

Configure Channel 12

OK 12

Cancel 12

Help 12

Set Module Address 13

Product Code 13

Serial Num 13

Address 13

Set Now 13

Autoset Module Address 13

Ok 13

Cancel 13

Configure Analog Input Modules 14

Enable Channel 14

Listner Mode 14

Tag 14

Description 15

Current Value 15

CM Parameters 15

Extra Commands 15

Reference 15

Engineering Units 15

Scaling 15

Auto Scale 15

Significant Change 16

Event Checking 16

Low and High Alarm Checking 16

Alarm Error Checking 17

Use Alpha Alarm Scheme 17

Configure Analog Output Modules 18

Enable Channel 18

Listner Mode 18

Tag 18

Description 18

Current Value 19

CM Parameters 19

Extra Commands 19

Reference 19

Engineering Units 19

Significant Change 19

Event Checking 19

Low and High Alarm Checking 20

Alarm Error Checking 20

Use Alpha Alarm Scheme 21

Configure Counter Input Modules 22

Enable Channel 22

Listner Mode 22

Tag 22

Description 22

Current Value 23

CM Parameters 23

Extra Commands 23

Engineering Units 23

Scaling 23

Auto Scale 23

Significant Change 23

Event Checking 24

Low and High Alarm Checking 24

Alarm Error Checking 25

Use Alpha Alarm Scheme 25

Configure Digital Input Channels. 26

Enable Channel 26

Listner Mode 26

Tag 26

Description 27

Current Value 27

CM Parameters 27

Extra Commands 27

Low State Description 27

High State Description 27

Event Checking 27

Alarm Error Checking 27

Alarms 27

Use Alpha Alarm Scheme 28

Configure Digital Output Channels. 29

Enable Channel 29

Listner Mode 29

Tag 29

Description 29

Current Value 30

CM Parameters 30

Extra Commands 30

Low State Description 30

High State Description 30

Event Checking 30

Alarm Error Checking 30

Alarms 30

Use Alpha Alarm Scheme 31

Interrogate Alpha Modules 32

Error Codes 34

Alpha Error Codes 34

Comms Error Codes 34

System Error Codes 35

Debug Facility 36

Switching Debugging On 36

Selecting the Debug Type 36

# Configuring an Alpha Device

The first time the system is configured it is necessary to enable and configure the way you wish the overall Alpha Device to operate. To configure the Alpha System either select **Devices** from the menu bar on the Main Window and then **Alpha** or double click the Alpha Icon in the Application Program Group.



To configure the operation of the whole Alpha Device choose the ***Advanced Configuration******Tab***.

To configure a Alpha Module point to the appropriate module in the ***Module Configuration Tab*** and double click.

# Advance Alpha Configuration

The Advanced Configuration windows appears as follows.



To ensure that the Aplha Service is included in the system check the **Auto-Enable Device** box.

## Alpha Scan Rate

The Alpha device can work in a dual ring mode. This allows a small number of channels to be sampled on the *FAST RING* more frequently than those on the *SLOW RING*. All channels on one Alpha Module are sampled at the same rate.

To set the rates, edit the text boxes associated with the Slow Ring A and the Fast Ring B. The values entered should take into account the number of channels on the Alpha Network. The times selected should be greater than the time taken for Alpha to sample all the configured channels. If a faster time or 0 (Zero) is entered then the device will scan as fast as possible. The Fast Ring must be a rate which is a multiple faster than that of Slow Ring.

## Save Outputs

To enable this utility check the Save Outputs flag. All values in output channels are saved to disk when the system is disabled. The next time the system is restarted the values which were previously in output channels will be restored to the appropriate channel number.

 **By Tag**

 Channel values can be saved and restored to channels using the channel tag instead of the channel number. In this way, channels can be rearranged within the modules and as long as the channel tags remain the same, the correct channel values will be restored to the appropriate channel number.

## Listener Mode

The Alpha Device can be configured so that all Channels are in Listener Mode. To enable this check the Listener Mode CheckBox

### Comm Port Settings

This dialog is used to configure the communications link between the Alpha Network and the computer. From the resulting Alpha Com Port dialog box complete as follows :



#### Network RS485

If we’re communicating through the RS485 Network then select this.option

#### Single RS232

If we’re communicating through an RS232 Link then select this option.

#### Comm Port

From the drop down list select the serial port to be used.

#### Baud Rate

Select appropriate baud rate for the link.

#### Read Outputs when not writing

Allows analog outputs to be read if they have not changed in the last scan

#### Read Outpts on initial scan

Reads outputs on the first scan

#### Use high speed 485

Check this option if the RS485 card is operating in high speed mode

#### Event Logging

Check this if you wish to output event data from modules

#### OK

Click on the OK button to accept the changes

#### Cancel

Selecting Cancel will abort any changes, reverting back to previous configuration of the port

# Configuring an Alpha Module

****

## Module Type

From the Module Type drop down list select the Alpha Module type to be configured. The module type number is prominent on the front of each Alpha Unit.

## Address

This specifies the address for this module. This can be set at configuration time using the ***Set*** button.

## Acquisition Rate

From the drop down list select the Acquisition Rate that this unit is to operate on.

## Auxiliary Channels

If this module support Auxiliary Channels the you will be given the option to use these channels as Auxiliary Outputs or to use them for the Alpha Alarm Scheme.

## Extra Command(n)

Up to six extra commands are added at installation time. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists. The function of these commands should be clear from their descriptors.

## Configure Channel

This button takes you to the Channel Configuration Dialog for the selected channel.

## OK

When advanced device configuration is complete click on this button to accept and move back to previous Window.

## Cancel

Nullify any changes made to both the module and channels configurations during this configuration session. The system will retain the previous configuration.

## Help

Online Help for Configuring Alpha Module.

### Set Module Address

This dialog allows the useer to set the module address given its Product Code and Serial Number.



#### Product Code

The field will display the module Product Code. The user cannot edit this field.

#### Serial Num

The user must enter the Serial Number of the connected module.

#### Address

The user must enter the Address that the module described by the above to fields should be set to.

#### Set Now

The ***Set Now*** button gives the user the ability to set the module address there and then. Default Communication Port settings are used if none have been configured through the Advanced Tab.

#### Autoset Module Address

This field instructs the driver to always set the Module Address at start-up.

#### Ok

Exits this dialog and saves options.

#### Cancel

Exits this dialog without saving options.

# Configure Analog Input Modules

##

## Enable Channel

The Enable Channel check box must be checked to enable, and allow this channel to be configured and ultimately included with all other configured channels in the overall System

## Listner Mode

To make make this channel operate in listener mode select this option.

## Tag

The tag is an 15 character alphanumeric field that can contain channel information or wiring schedule references.

## Description

The Description field is a 32 character alphanumeric field in which a description of the channel can be detailed.

## Current Value

Displays the current value of this channel if the scanner is running else it displays “\*\*\*Disabled\*\*\*”

## CM Parameters

Up to 4 fields will be added at installation time. These alow the user to select the parameter values for the CM command. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists The values for these fields will be downloaded to the Alpha Module at run-time. The function of these fields should be clear from their descriptors.

## Extra Commands

Up to two extra commands are added at installation time. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists. The function of these commands should be clear from their descriptors.

## Reference

When the **Reference** check box is checked then this channel has been defined as a  *Reference Channel*. Values of a Reference channel are displayed as the measured value - zero (reference) value. When the System is enabled the zero value can be initialized using one of the following methods::

i) From the Alpha Device Main Window choose **Initialize** from the **Control**

menu.

ii) From the Main Window choose **Initialise** from the **Control**  menu.

iii) Press the keys **CTRL** + **I** together.

## Engineering Units

 **Minimum**

 Minimum engineering value for all analog channels in addition to the unit field. The default is 0

 **Maximum**

Maximum engineering value for all analog channels in addition to the unit field. The default is 100

**Descriptor**

An 8 character field available to describe the units of the measurement

## Scaling

To enable the utility check the Scaling Check box. The **Slope**  and **Offset**  values can be entered directly into the text boxes. The formula applied is:

 y = mx + c where: m is SLOPE

 x is the measured value.

 c is the OFFSET

## Auto Scale

Click On the Auto Scale button if you want the scale and offset values calculated automatically. In the dialog box enter the values in the text boxes. The low measured value, and the high measured value, the output range of the transducer.

|  |
| --- |
| **NB.****Scaling will not be applied to the channel, even if the system is enabled, until the system is next enabled or the Alpha Device is reconfigured.**  |

## Significant Change

To enable the Significant Change feature check the **Sig Change**  check box. This facility allows filtering of data on channels on which significant change is of interest. Such changes can cause an event, which can be logged.

The figure entered in the **Value** text box, in engineering units is the rate of change that if the measured channel exceeds per scan, either increasing or decreasing will cause the significant change event trigger. The scan rate is determined in the Advanced Configuration Tab.

If a logger is configured in Event mode, or Period-Event, each time the significant change trigger operates information on the channels defined in the logger will be recorded . A significant change event only lasts one scan, unless the next reading also changes greater than the Significant change value

When monitoring channels, if the Significant Change is triggered, then the fact will be annotated alongside the other channel information in the Monitor Window.

The significant change events are in addition to those caused by an *Event*.

## Event Checking

Event checking is used, if required to trigger a logger to record information on a number of channels during an event. Check the **Event Checking**  check box if this facility is needed.

**High Limit**

A value, in engineering units, entered in this text box will define the level that, if

exceeded, will cause an event trigger.

**Low Limit**

A value entered in this text box will define the level that if the channel result falls below

will cause an event trigger.

## Low and High Alarm Checking

Alarm checking is available on all channels throughout the system. **Low Alarm** and  **High Alarm** levels can be configured independent of each other. All the values entered are in engineering units. If a channel reading exceeds the High Alarm limit then an alarm will be triggered as it will if the channel goes below the Low Alarm limit.

When monitoring channels, if the high or low alarm is triggered, then the fact will be annotated alongside the other channel information in the Monitor Window.

**Enable Alarm Checking**

Check either the **Low Alarm Checking** or **High Alarm Checking** or both check boxes to enable the facility.

**Drive Common Alarm**

A common alarm is a single digital output which will switch on when any channel with the Drive Common Alarm enabled goes into an alarm state.

Check this box if a link to the Common Alarm is required.

**Alarm Limit**

The value at which the channel will flag an alarm

**Warning and Limit (Analog channel only)**

If required, a warning can be displayed when a channel reaches a limit close to the alarm limit. For low alarm checking, the limit must be less than the alarm limit. For high alarm checking, the warning limit must be less than the alarm limit

**Hysteresis**

Check the box if this feature if needed. Enter the value of the dead band in the text box.

Hysteresis can prevent 'noisy' channels from reporting multiple alarms when the average reading is close to the alarm or warning threshold. **The Hysteresis value is relative to the warning or alarm limit.**

**Priority**

Enter or edit the number in the text box to allocate the priority of this alarm.

**Alarm Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the system flagging an alarm.

**Alarm Message**

An Alarm Message can be defined to be displayed on the Status line of the application Main Window when a channel goes into an alarm state.

Enter the message, up to 32 characters.

## Alarm Error Checking

 **Drive Common**

A common alarm is a single digital output which will switch on when any channel with the **Drive Common Alarm** enabled goes into an alarm state.

Check this box if a link to the Common Alarm is required.

 **Priority**

 Enter or edit the number in the text box to allocate the priority of this channels alarm.

 **Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the system

 flagging an alarm.

## Use Alpha Alarm Scheme

If this option is present it allows the Alarm Limits to be dowloaded to the Alpha Module. These limits will be used to drive the Alpha Alarm Channel.

# Configure Analog Output Modules

##

## Enable Channel

The Enable Channel check box must be checked to enable, and allow this channel to be configured and ultimately included with all other configured channels in the overall System

## Listner Mode

To make make this channel operate in listener mode select this option.

## Tag

The tag is an 15 character alphanumeric field that can contain channel information or wiring schedule references.

## Description

The Description field is a 32 character alphanumeric field in which a description of the channel can be detailed.

## Current Value

Displays the current value of this channel if the scanner is running else it displays “\*\*\*Disabled\*\*\*”

## CM Parameters

Up to 4 fields will be added at installation time. These alow the user to select the parameter values for the CM command. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists The values for these fields will be downloaded to the Alpha Module at run-time. The function of these fields should be clear from their descriptors.

## Extra Commands

Up to two extra commands are added at installation time. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists. The function of these commands should be clear from their descriptors.

## Reference

When the **Reference** check box is checked then this channel has been defined as a  *Reference Channel*. Values of a Reference channel are displayed as the measured value - zero (reference) value. When the System is enabled the zero value can be initialized using one of the following methods::

i) From the Alpha Device Main Window choose **Initialize** from the **Control**

menu.

ii) From the Main Window choose **Initialise** from the **Control**  menu.

iii) Press the keys **CTRL** + **I** together.

## Engineering Units

**Minimum**

Minimum engineering value for all analog channels in addition to the unit field. The default is 0

**Maximum**

Maximum engineering value for all analog channels in addition to the unit field. The default is

100

**Descriptor**

An 8 character field available to describe the units of the measurement

## Significant Change

To enable the Significant Change feature check the **Sig Change**  check box. This facility allows filtering of data on channels on which significant change is of interest. Such changes can cause an event, which can be logged.

The figure entered in the **Value** text box, in engineering units is the rate of change that if the measured channel exceeds per scan, either increasing or decreasing will cause the significant change event trigger. The scan rate is determined in the Advanced Configuration Tab.

If a logger is configured in Event mode, or Period-Event, each time the significant change trigger operates information on the channels defined in the logger will be recorded . A significant change event only lasts one scan, unless the next reading also changes greater than the Significant change value

When monitoring channels, if the Significant Change is triggered, then the fact will be annotated alongside the other channel information in the Monitor Window.

The significant change events are in addition to those caused by an *Event*.

## Event Checking

Event checking is used, if required to trigger a logger to record information on a number of channels during an event. Check the **Event Checking**  check box if this facility is needed.

**High Limit**

A value, in engineering units, entered in this text box will define the level that, if exceeded, will cause an event trigger.

**Low Limit**

A value entered in this text box will define the level that if the channel result falls below will cause an event trigger.

## Low and High Alarm Checking

Alarm checking is available on all channels throughout the system. **Low Alarm** and  **High Alarm** levels can be configured independent of each other. All the values entered are in engineering units. If a channel reading exceeds the High Alarm limit then an alarm will be triggered as it will if the channel goes below the Low Alarm limit.

When monitoring channels, if the high or low alarm is triggered, then the fact will be annotated alongside the other channel information in the Monitor Window.

**Enable Alarm Checking**

Check either the **Low Alarm Checking** or **High Alarm Checking** or both check boxes to enable the facility.

**Drive Common Alarm**

A common alarm is a single digital output which will switch on when any channel with the Drive Common Alarm enabled goes into an alarm state.

Check this box if a link to the Common Alarm is required.

**Alarm Limit**

The value at which the channel will flag an alarm

**Warning and Limit (Analog channel only)**

If required, a warning can be displayed when a channel reaches a limit close to the alarm limit. For low alarm checking, the limit must be less than the alarm limit. For high alarm checking, the warning limit must be less than the alarm limit

**Hysteresis**

Check the box if this feature if needed. Enter the value of the dead band in the text box.

Hysteresis can prevent 'noisy' channels from reporting multiple alarms when the average reading is close to the alarm or warning threshold. **The Hysteresis value is relative to the warning or alarm limit.**

**Priority**

Enter or edit the number in the text box to allocate the priority of this alarm.

**Alarm Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the system flagging an alarm.

**Alarm Message**

An Alarm Message can be defined to be displayed on the Status line of the application Main Window when a channel goes into an alarm state.

Enter the message, up to 32 characters.

## Alarm Error Checking

 **Drive Common**

A common alarm is a single digital output which will switch on when any channel with the **Drive Common Alarm** enabled goes into an alarm state.

Check this box if a link to the Common Alarm is required.

 **Priority**

 Enter or edit the number in the text box to allocate the priority of this channels alarm.

 **Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the system flagging an alarm.

## Use Alpha Alarm Scheme

If this option is present it allows the Alarm Limits to be downloaded to the Alpha Module. These limits will be used to drive the Alpha Alarm Channel.

# Configure Counter Input Modules



## Enable Channel

The Enable Channel check box must be checked to enable, and allow this channel to be configured and ultimately included with all other configured channels in the overall System

## Listener Mode

To make this channel operate in listener mode select this option.

## Tag

The tag is an 15 character alphanumeric field that can contain channel information or wiring schedule references.

## Description

The Description field is a 32 character alphanumeric field in which a description of the channel can be detailed.

## Current Value

Displays the current value of this channel if the scanner is running else it displays “\*\*\*Disabled\*\*\*”

## CM Parameters

Up to 4 fields will be added at installation time. These allow the user to select the parameter values for the CM command. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists The values for these fields will be downloaded to the Alpha Module at run-time. The function of these fields should be clear from their descriptors.

## Extra Commands

Up to two extra commands are added at installation time. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists. The function of these commands should be clear from their descriptors.

## Engineering Units

**Minimum**

Minimum engineering value for all analog channels in addition to the unit field. The default is 0

**Maximum**

Maximum engineering value for all analog channels in addition to the unit field. The default is

100

**Descriptor**

An 8 character field available to describe the units of the measurement

## Scaling

To enable the utility check the Scaling Check box. The **Slope**  and **Offset**  values can be entered directly into the text boxes. The formula applied is:

 y = mx + c where: m is SLOPE

 x is the measured value.

 c is the OFFSET

## Auto Scale

Click On the Auto Scale button if you want the scale and offset values calculated automatically. In the dialog box enter the values in the text boxes. The low measured value, and the high measured value, the output range of the transducer.

|  |
| --- |
| **NB.****Scaling will not be applied to the channel, even if the system is enabled, until the system is next enabled or the Alpha Device is reconfigured.**  |

## Significant Change

To enable the Significant Change feature check the **Sig Change**  check box. This facility allows filtering of data on channels on which significant change is of interest. Such changes can cause an event, which can be logged.

The figure entered in the **Value** text box, in engineering units is the rate of change that if the measured channel exceeds per scan, either increasing or decreasing will cause the significant change event trigger. The scan rate is determined in the Advanced Configuration Tab.

If a logger is configured in Event mode, or Period-Event, each time the significant change trigger operates information on the channels defined in the logger will be recorded . A significant change event only lasts one scan, unless the next reading also changes greater than the Significant change value

When monitoring channels, if the Significant Change is triggered, then the fact will be annotated alongside the other channel information in the Monitor Window.

The significant change events are in addition to those caused by an *Event*.

## Event Checking

Event checking is used, if required to trigger a logger to record information on a number of channels during an event. Check the **Event Checking**  check box if this facility is needed.

**High Limit**

A value, in engineering units, entered in this text box will define the level that, if exceeded, will cause an event trigger.

**Low Limit**

A value entered in this text box will define the level that if the channel result falls below will cause an event trigger.

## Low and High Alarm Checking

Alarm checking is available on all channels throughout the system. **Low Alarm** and  **High Alarm** levels can be configured independent of each other. All the values entered are in engineering units. If a channel reading exceeds the High Alarm limit then an alarm will be triggered as it will if the channel goes below the Low Alarm limit.

When monitoring channels, if the high or low alarm is triggered, then the fact will be annotated alongside the other channel information in the Monitor Window.

**Enable Alarm Checking**

Check either the **Low Alarm Checking** or **High Alarm Checking** or both check boxes to enable the facility.

**Drive Common Alarm**

A common alarm is a single digital output which will switch on when any channel with the Drive Common Alarm enabled goes into an alarm state.

Check this box if a link to the Common Alarm is required.

**Alarm Limit**

The value at which the channel will flag an alarm

**Warning and Limit (Analog channel only)**

If required, a warning can be displayed when a channel reaches a limit close to the alarm limit. For low alarm checking, the limit must be less than the alarm limit. For high alarm checking, the warning limit must be less than the alarm limit

**Hysteresis**

Check the box if this feature if needed. Enter the value of the dead band in the text box.

Hysteresis can prevent 'noisy' channels from reporting multiple alarms when the average reading is close to the alarm or warning threshold. **The Hysteresis value is relative to the warning or alarm limit.**

**Priority**

Enter or edit the number in the text box to allocate the priority of this alarm.

**Alarm Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the system flagging an alarm.

**Alarm Message**

An Alarm Message can be defined to be displayed on the Status line of the application Main Window when a channel goes into an alarm state.

Enter the message, up to 32 characters.

## Alarm Error Checking

 **Drive Common**

A common alarm is a single digital output which will switch on when any channel with the **Drive**

 **Common Alarm** enabled goes into an alarm state.

 Check this box if a link to the Common Alarm is required.

 **Priority**

 Enter or edit the number in the text box to allocate the priority of this channels alarm.

 **Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the

system flagging an alarm.

## Use Alpha Alarm Scheme

If this option is present it allows the Alarm Limits to be downloaded to the Alpha Module. These limits will be used to drive the Alpha Alarm Channel.

# Configure Digital Input Channels.

##

## Enable Channel

The Enable Channel check box must be checked to enable, and allow this channel to be configured and ultimately included with all other configured channels in the System.

## Listener Mode

To make this channel operate in listener mode select this option.

## Tag

The Tag field is an 12 character alphanumeric field that can contain channel information or wiring schedule references.

## Description

The Description field is a 16 character alphanumeric field in which a description of the channel can be detailed.

## Current Value

Displays the current value of this channel if the scanner is running else it displays “\*\*\*Disabled\*\*\*”

## CM Parameters

Up to 4 fields will be added at installation time. These alow the user to select the parameter values for the CM command. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists The values for these fields will be downloaded to the Alpha Module at run-time. The function of these fields should be clear from their descriptors.

## Extra Commands

Up to two extra commands are added at installation time. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists. The function of these commands should be clear from their descriptors.

## Low State Description

A 32 character field in which to enter a description of the low state of the channel.

## High State Description

A 32 character field in which to enter a description of the high state of the channel.

## Event Checking

Event checking is used, if required to trigger a logger to record information on an event. If this facility is required click on the drop down list box and select OFF, HIGH STATE, or LOW STATE as appropriate

## Alarm Error Checking

 **Drive Common**

A common alarm is a single digital output which will switch on when any channel with the **Drive**

 **Common Alarm** enabled goes into an alarm state.

 Check this box if a link to the Common Alarm is required.

 **Priority**

 Enter or edit the number in the text box to allocate the priority of this channels alarm.

 **Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the

system flagging an alarm.

## Alarms

**Alarm State**

Alarm checking is available on all channels throughout the System. To configure alarm checking on this channel click on the drop down box and select OFF, HIGH STATE, or LOW STATE as appropriate. If the channel's output state changes to an Alarm State an alarm will be triggered on the channel. When monitoring channels, if the alarm is triggered, the fact will be annotated alongside the other channel information in the Monitor Window.

**Alarm Priority**

Enter the priority of the alarm triggered by this channel.

**Common Alarm**

Channels can be configured to trigger a Common Alarm. A common alarm is a single digital output which will switch on when any channel with the Drive Common Alarm enabled goes into an alarm state.

**Alarm Message**

An Alarm Message can be defined to be displayed on the Status line of the Main Window when a channel goes into an alarm state.

## Use Alpha Alarm Scheme

If this option is present it allows the Alarm Limits to be dowloaded to the Alpha Module. These limits will be used to drive the Alpha Alarm Channel.

# Configure Digital Output Channels.



## Enable Channel

The Enable Channel check box must be checked to enable, and allow this channel to be configured and ultimately included with all other configured channels in the System.

## Listner Mode

To make make this channel operate in listener mode select this option.

## Tag

The Tag field is an 12 character alphanumeric field that can contain channel information or wiring schedule references.

## Description

The Description field is a 16 character alphanumeric field in which a description of the channel can be detailed.

## Current Value

Displays the current value of this channel if the scanner is running else it displays “\*\*\*Disabled\*\*\*”

## CM Parameters

Up to 4 fields will be added at installation time. These alow the user to select the parameter values for the CM command. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists The values for these fields will be downloaded to the Alpha Module at run-time. The function of these fields should be clear from their descriptors.

## Extra Commands

Up to two extra commands are added at installation time. These can take the form of Edit Boxes, Check Boxes or Drop Down Lists. The function of these commands should be clear from their descriptors.

## Low State Description

A 32 character field in which to enter a description of the low state of the channel.

## High State Description

A 32 character field in which to enter a description of the high state of the channel.

## Event Checking

Event checking is used, if required to trigger a logger to record information on an event. If this facility is required click on the drop down list box and select OFF, HIGH STATE, or LOW STATE as appropriate.

## Alarm Error Checking

 **Drive Common**

A common alarm is a single digital output which will switch on when any channel with the **Drive**

 **Common Alarm** enabled goes into an alarm state.

 Check this box if a link to the Common Alarm is required.

 **Priority**

 Enter or edit the number in the text box to allocate the priority of this channels alarm.

 **Delay**

Enter the time, in seconds, between the channel value entering the alarm state and the

system flagging an alarm.

## Alarms

**Alarm State**

Alarm checking is available on all channels throughout the System. To configure alarm checking on this channel click on the drop down box and select OFF, HIGH STATE, or LOW STATE as appropriate. If the channel's output state changes to an Alarm State an alarm will be triggered on the channel. When monitoring channels, if the alarm is triggered, the fact will be annotated alongside the other channel information in the Monitor Window.

**Alarm Priority**

Enter the priority of the alarm triggered by this channel.

**Common Alarm**

Channels can be configured to trigger a Common Alarm. A common alarm is a single digital output which will switch on when any channel with the Drive Common Alarm enabled goes into an alarm state.

**Alarm Message**

An Alarm Message can be defined to be displayed on the Status line of the Main Window when a channel goes into an alarm state.

## Use Alpha Alarm Scheme

If this option is present it allows the Alarm Limits to be dowloaded to the Alpha Module. These limits will be used to drive the Alpha Alarm Channel.

# Interrogate Alpha Modules

The user can interrogate the alpha module to determine what modules are present on the Network and read there configuration into the next available slot.

This can be achieved by clicking on the ***Network Modules*** option in the Edit menu. The user will be presented with the following dialog:



The range limits for the address of the modules to search for must first be entered.

**Note: The more modules in the search the longer this will take.**

When Searching is complete the user is presented with the following listview:



The left hand pane describes the modules that are currently configured in the system whilst the right hand pane displays the details for the modules that where within the search range.

By clicking the ***Read*** button any modules that appear in the right hand pane and don’t have a corresponding module in the left hand pane (i.e. the address doesn’t appear in the left hand pane) will have their configuration copied into the system.

# Error Codes

Error messages will be reported to users in the Error Banner of both the Main Application and the Alpha Configurations Main View. They will take the following format:

M:nnn XX A:nnn C:nnn S:nnnnn

M: - Details the Module reporting the error.

XX - Details the Command causing the error.

A: - Details the associated Alpha error code.

C: - Details the associated Comms error code.if appropriate.

S: - Details the associated System error code if appropriate.

## Alpha Error Codes

|  |  |
| --- | --- |
| 001  |  If this code appears you should look to the C: to get a descrition of the problem |
| 002  |  The selected baudrate is unsupported on this system |
| 003  |  Not all of the packet was received within the timeout period for the command |
| 004  |  The packing framing characters received were incorrect |
| 005  |  A invalid checksum was received |
| 006  |  An address was expected int the packet but was not found |
| 007  |  An unkown command was sent to the module |
| 008  |  The parameters sent with this request were unexpected |
| 009  |  The parameter sent with this command was out of range |
| 010  |  The channel range specified for this command was invalid |
| 011  |  No data was returned for the query |
| 012  |  Unkown error returned from the Alpha |
| 013  |  The return address on the packet was not what was expected |
| 014  |  Unexpected address for this command |
| 015  |  The contents of the returned packet was unexpected |
| 016  |  An unexpected token was encountered int he return packet |
| 017  |  The start channel number for the data packet was not what was expected |
| 018  |  The data packet was incomplete |
| 019  |  The returned data format was not what was expected |
| 020  |  An invlaid range of channels was requested |
| 021  |  The channel range in the return packet was unexpected |
| 022  |  The report format of the return packet was unexpected |
| 023 |  The data packet received exceeds that which was expected |

## Comms Error Codes

|  |  |
| --- | --- |
| 001  |  If this code appears you should look to the S: to get a descrition of the problem |
| 002  |  The selected communication port is already in use |
| 003  |  Could not write all the data to the communication port |
| 004  |  Could not read all the requested data on the communication port |
| 005  |  The operation being performed on the communication port timed out |
| 006  |  The communications handle is invalid |
| 007 |  The hardware detected a break condition |
| 008 |  **Windows 95/98/Me:** A parallel device is not selected |
| 009 |  The hardware detected a framing error |
| 010 |  An I/O error occurred during communications with the device |
| 011 |  The requested mode is not supported |
| 012 |  **Windows 95/98/Me:** A parallel device signaled that it is out of paper |
| 013 |  A character-buffer overrun has occurred. The next character is lost |
| 014 |  **Windows 95/98/Me:** A time-out occurred on a parallel device |
| 015 |  An input buffer overflow has occurred. There is either no room in the input buffer, or a  character was received after the end-of-file (EOF) character |
| 016 |  The hardware detected a parity error |
| 017 |  The application tried to transmit a character, but the output buffer was full |
| 018 |  An unknown error was encountered |

## System Error Codes

Refer to the operating system documentation.

# Debug Facility

The Alpha driver contains a debug facility which allows it to be debugged at run-time should an error occur. To enable this facility a number of **Registry Entries** must be set:

## Switching Debugging On

To switch debugging on simply add the following registry key

***HKEY\_LOCAL\_MACHINE\SOFTWARE\Measuresoft\<ProductName>\ALPHA\_<dev\_number>\_Debug*** and set its value to “**ON”.**

## Selecting the Debug Type

The Alpha Driver allows you to output the debug information to a Console Window, Text File or as a Trace Statement which can be displayed by applications such as DBWIN32.EXE. To enable these facilities add the following registry key

 ***HKEY\_LOCAL\_MACHINE\SOFTWARE\Measuresoft\<ProductName>\ALPHA\_<dev\_number>\_DebugType***

The values of this key can be as follows:

**“CON”** to send output to a console window

**“FILE”** to send the output to a text file or

**“TRACE”** to send the output as a trace statement.

These can be concatenated to send the output to multiple types by using the **|** symbol.

e.g. “**FILE|CON”** would send the output to both File and Console Window.

When sending output to the **FILE** type you must specify the file. To do this add the following registry entry

HKEY\_LOCAL\_MACHINE\SOFTWARE\Measuresoft\<ProductName>\ALPHA\_<dev\_number>\_DebugFile

Its value should contain the name of the file you wish to output debug information too.

The number of bytes received and transmitted can be stored in a user analog channel.

To enable counting add the following registry keys

 ***HKEY\_LOCAL\_MACHINE\SOFTWARE\Measuresoft\<ProductName>\ALPHA\_<dev\_number>\_DebugRxCount***

***HKEY\_LOCAL\_MACHINE\SOFTWARE\Measuresoft\<ProductName>\ALPHA\_<dev\_number>\_DebugTxCount***

The values of these keys specify a channel used to store the count e.g. P1

The channel used must be configured. To reset the counts, use a calculation function.

**Note:** Debugging must be switched ON

**Note:** Console (CON) is not supported on Windows Vista. Instead set the output mode to TRACE, and to view the debug data you must use SysInternals Debug Viewer. This can be downloaded from <http://www.microsoft.com/technet/sysinternals/Utilities/DebugView.mspx>

In order for Console mode to work on Windows XP the service must be configured to logon as the System Account with Interact with Desktop enabled

# Extra User Commands

The Alpha driver contains a facility to allow a set of commands to be downloaded to the Alpha at various points in the scanning cycle. The commands can be configured in the following files in the ALPHA\_<n> subdirectory of the CURRENT\_CONFIG directory.

Open.txt – When communication to the Alpha network is initially established

Config.txt - – When configuration is downloaded to the Alpha

Initialise.txt – When analog input channels are initialized to zero readings

Reset.txt – When counter channels are reset to sero

Close.txt - When communication to the Alpha network is shut down

The format of the lines in these file for commands not expecting a response is as follows:

0,0,Command

The format of the lines in these file for commands not expecting a response is as follows:

1,<timeout in milliseconds>,Command

e.g.

 1,300,@01:AO1